GTZ-843 转速频率控制仪 简易接线说明

一、仪表工作电源

从第13、14号接线端子接入 交流85~265V 或 直流110~250V

二、发电机残压

从第1、2号接线端子接入发电机机端电压 AC100V

三、转速信号百分比输出接点：J1-J8继电器

5%   转速信号输出接点 J1 对应接线端子 A1、B1 报警1

35%  转速信号输出接点 J2 对应接线端子 A2、B2 报警2

50%  转速信号输出接点 J3 对应接线端子 A3、B3 报警3

80%  转速信号输出接点 J4 对应接线端子 A4、B4 报警4

95%  转速信号输出接点 J5 对应接线端子 A5、B5 报警5

115% 转速信号输出接点 J6 对应接线端子 A6、B6 报警6

140% 转速信号输出接点 J7 对应接线端子 A7、B7 报警7

140% 转速信号输出接点 J8 对应接线端子 A8、B8 报警8

Wiring description of GTZ-843 speed and frequency controller

一、Instrument working power supply

Pin13、Pin14 input AC 85-265V or DC 110-250V

二、Generator voltage signal input (Generator PT Voltage transformer)

Pin1、Pin2 input  Generator PT Voltage AC100V

三、Speed signal percentage output：J1-J8  relay

5%   Speed signal J1 Corresponding output A1、B1 (ALM 1)

35%  Speed signal J2 Corresponding output A2、B2 (ALM 2)

50%  Speed signal J3 Corresponding output A3、B3 (ALM 3)

80%  Speed signal J4 Corresponding output A4、B4 (ALM 4)

95%  Speed signal J5 Corresponding output A5、B5 (ALM 5)

115% Speed signal J6 Corresponding output A6、B6 (ALM 6)

140% Speed signal J7 Corresponding output A7、B7 (ALM 7)

140% Speed signal J8 Corresponding output A8、B8 (ALM 8)